Polargy PolarPlexTM

Standard Containment Panels

PART 1 - GENERAL

  - SUMMARY

- Vertical Containment Panels used for either Hot or Cold Aisle Containment.

  - SYSTEM DESCRIPTION

- Vertical Panels.

1.3	DESIGN REQUIREMENTS

- Vertical Panels shall be individual aluminum framed panels with twinwall polycarbonate inserts. Panel twinwall inserts shall be Class A fire-rated material.

- Vertical Panels shall be individual panels that are tool-lessly and easily removable so that the panels can be removed for maintenance access to the space above the equipment racks and for cleaning of the panels.

1.4	WARRANTY

- Standard Panels shall be warranted against defects in materials and workmanship for a one-year period for the first 12 months after initial start-up or 18 months after ship date, whichever occurs first.

PART 2 – PRODUCTS

2.1	MANUFACTURERS

- Basis of Design: Product specified is the PolarPlexTM Standard Panel as manufactured by Polargy, Inc.

- Substitutions: Proposed substitutions must be approved prior to bidding.

2.2	GENERAL

- The vertical panels shall be supported by a Unistrut/F-bracket track installed along the top of the equipment racks.

- The standard vertical panels shall be hot or cold aisle containment panels supported by a Unistrut/F-bracket track installed along the top of the equipment racks (or the F-bracket shall be directly secured to the equipment cabinets if rack independence is not needed.)

2.3	STRUCTURE

- Vertical panels shall be tool-lessly removable and held at the bottom in the F-bracket/Unistrut track that runs along the tops of the equipment racks. For closed top architectures vertical panels shall be supported at the top with a ceiling trim piece and 3M Dual-Lock. For open top architectures, the vertical panels shall be aligned at their tops with U-channel pieces that connect adjacent panels.

- Vertical Panels shall be prefabricated in order to minimize installation time.

- Vertical Panels shall be individual panels no wider than 48”. Panels shall be aluminum-framed panels with 8mm thick twin-wall polycarbonate inserts. Panel frame members shall be lightweight anodized aluminum with a 1” tall profile. Each panel shall be installed and removed easily without tools to allow for easy cleaning and maintenance access.

PART 3 – EXECUTION

3.1 	PREPARATION

- Cabinets to which doors are attached should be level and square and properly secured to the floor.

3.2 	INSTALLATION

- Install Standard Panels in accordance with manufacturer's shop drawings and written instructions.

- Panels shall be supported in the F-Bracket/Unistrut track on the bottom. If rack independence is not needed then the F-Bracket must be secured directly to the tops of the equipment cabinets.

- Installers shall provide appropriate installation hardware as defined by local code or the authority having jurisdiction (AHJ).

3.3 	ADJUSTING AND CLEANING

- Clean panels with mild soap and water solution as needed.

END OF SECTION